## Madison Township Fire Department

## Guidelines For New Construction

Based upon Ohio Fire Code (2011 Edition)

The Madison Township Fire Department, being the Fire Authority Having Jurisdiction (AHJ), has established the following Fire Protection Guidelines, to aid developers and architects planning new construction within its jurisdictional boundaries (Madison Township, Groveport, Canal Winchester and Obetz,). Some items may not be required depending on the type of occupancy, use group classification, and overall size of the structure, facility, or subdivision being constructed.

Proper State of Ohio licensing and certifications of contractors and subcontractors SHALL be verified by the Fire AHJ and Chief Building Official during the construction process.

- We highly encourage all prospective developers and contractors to setup a preconstruction meeting to review these MTFD requirements during their project planning process. Any and all building owner(s) / occupant(s) contractors, vendors, landlords, etc. should become familiar with these requirements.

Please incorporate the following items as a part of your overall plan development process.

Construction Documents:

Construction documents for proposed fire apparatus access, location of fire lanes, security gates across fire apparatus access and construction documents and hydraulic calculations for fire hydrant systems SHALL be submitted to the fire department for review and approval prior to construction.

Timing of Installation:

When fire apparatus access roads or a water supply for fire protection is required to be installed, such protection SHALL be installed and made serviceable prior to and during the time of construction except when approved alternative methods of protection are provided. Temporary street signs SHALL be installed at each street intersection when construction of new roadways allows passage by vehicles.

Fire Apparatus Access Roads:

Where required:

Fire apparatus access roads shall be provided and maintained

Buildings and Facilities:

Approved fire apparatus access roads SHALL be provided for every facility, building or portion of a building hereafter constructed or moved into or within the jurisdiction which are not readily accessible from a public and/or private street. The fire apparatus access road SHALL comply with the requirements of the Ohio Fire Code and SHALL extend to within 150 feet of all portions of the facility and all portions of the exterior walls of the first story of the building as measured by an approved route around the exterior of the building or facility.

Exception: The fire code official is authorized to increase the dimension of 150 feet where:

1. The building is equipped throughout with an approved automatic sprinkler system installed in accordance of rule 1301:7-7-09 of the Administrative Code.

2. Fire apparatus access roads cannot be installed because of location on property, topography, waterways, nonnegotiable grades or other similar conditions, and an approved alternative means of fire protection is provided.

Additional access:

The fire code official is authorized to require more than one fire apparatus access road based on the potential for impairment of a single road by vehicle congestion, condition of terrain, climatic conditions or other factors that could limit access.

High-piled storage:

Fire department vehicle access to buildings used for high-piled combustible storage SHALL comply with the applicable provisions of rule 1301:7-7-23 of the Administrative Code.

Dimensions:

Public / private road / street widths SHALL be a minimum of 26 feet in width for Commercial / Industrial Development, and a minimum of 26 feet in width for Planned Subdivision Development (Unobstructed, Islands in entrances, Cul-de-sacs, etc., SHALL not be included in the calculation for street widths.), and an unobstructed vertical clearance of not less than 13 feet 6 inches.

**Access SHALL be maintained during construction phase.

Authority

The fire code official SHALL have the authority to require an increase in the minimum access widths where they are inadequate for fire or rescue operations.

Surface:

Fire apparatus access roads SHALL be designed and maintained to support the imposed loads of fire apparatus and SHALL be surfaced so as to provide all-weather driving capabilities.

Turning radius:

The required turning radius of a fire apparatus access road SHALL be determined by the fire code official.

LOCAL REQUIREMENT:  Fire Lane Locations and signage requires prior approval and SHALL be determined by the Fire Code Official on a case by case basis.  Areas where fire lanes are normally required include access points deemed critical to firefighting operations, fire hydrant locations, Fire Department connections (FDC), Post Indicator Valve Locations, and Fire Pump Control Locations.

Commercial / Industrial / Factory Buildings:  Fire Apparatus Access Lanes SHALL be posted on both sides of the Fire Apparatus Access Road  (Fire Lane) with signage every 100 feet on unpaved roadways.

In paved areas, signage and striping of the Fire Lane SHALL also be required with the curbs painted a contrasting color (preferably yellow).  Signage and striping or curb painting would be required at all fire hydrant locations (paved areas).  In locations where tractor-trailers are staged, the striping SHALL extend to 10 feet in width on both sides of a fire hydrant or other fire control appurtenance and extend in depth the entire length of the tractor-trailers being staged.

Dead-End Fire Apparatus Access Roads in excess of 150 feet in length SHALL be provided with an area for turning around fire apparatus.  Prior review and approval of the Fire AHJ SHALL be required.

Dead ends:

Dead-end fire apparatus access roads in excess of 150 feet in length SHALL be provided with an approved area for turning around fire apparatus.

Bridges and elevated surfaces:

Where a bridge or an elevated surface is part of a fire apparatus access road, the bridge SHALL be constructed and maintained in accordance with AASHTO HB-17 as listed in rule 1301:7-7-47 of the Administrative Code. Bridges and elevated surfaces SHALL be designed for a live load sufficient to carry the imposed loads of fire apparatus. Vehicle load limits SHALL be posted at both entrances to bridges when required by the fire code official. Where elevated surfaces designed for emergency vehicle use are adjacent to surfaces which are not designed for such use, approved barriers, approved signs or both SHALL be installed and maintained when required by the fire code official.

Grade:

The grade of the fire apparatus access road SHALL be within the limits established by the fire code official based on the fire department’s apparatus.

Angles of Approach and Departure:

The angles of approach and departure for fire apparatus access roads SHALL be within the limits established by the fire code official based on the fire department’s apparatus.

Marking:

Where required by the fire code official, approved signs or other approved notices or markings that include the words "NO PARKING—FIRE LANE" SHALL be provided for fire apparatus access roads to identify such roads or prohibit the obstruction thereof. The means by which fire lanes are designated SHALL be maintained in a clean and legible condition at all times and be replaced or repaired when necessary to provide adequate visibility.

Obstruction of Fire Apparatus Access Roads:

Fire apparatus access roads SHALL not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established by the AHJ SHALL be maintained at all times.

Required Gates or Barricades:

The fire code official is authorized to require the installation and maintenance of gates or other approved barricades across fire apparatus access roads, trails or other access ways, not including public streets, alleys or highways. Electric gate operators, where provided, SHALL be listed in accordance with UL 325 as listed in rule 1301:7-7-47 of the Administrative Code. Gates intended for automatic operation SHALL be designed, constructed and installed to comply with the requirements of ASTM F 2200 as listed in rule 1301:7-7-47 of the Administrative Code.

Secured gates and barricades:

When required, gates and barricades SHALL be secured in an approved manner. Roads, trails and other access ways that have been closed and obstructed SHALL not be trespassed on or used unless authorized by the owner and the fire code official.

Exception: The restriction on use SHALL not apply to public officers acting within the scope of duty.

Security gates:

The installation of security gates across a fire apparatus access road SHALL be approved by the fire code official. Where security gates are installed, they SHALL have an approved means of emergency operation. The security gates and the emergency operation SHALL be maintained operational at all times. Electric gate operators, where provided, SHALL be listed in accordance with UL 325 as listed in rule 1301:7-7-47 of the Administrative Code. Gates intended for automatic operation SHALL be designed, constructed and installed to comply with the requirements of ASTM F 2200 as listed in rule 1301:7-7-47 of the Administrative Code.

Premises Identification:

Address Numbers:

New and existing buildings SHALL have approved address numbers, building numbers or approved building identification placed in a position that is plainly legible and visible from the street or road fronting the property. These numbers SHALL contrast with their background. Address numbers SHALL be Arabic numbers. Numbers SHALL be a minimum of 4 inches  high with a minimum stroke width of 0.5 inch Where access is by means of a private road and the building cannot be viewed from the public way, a monument, pole or other sign or means SHALL be used to identify the structure.

Street or road signs:

Streets and roads SHALL be identified with approved signs. Temporary signs SHALL be installed at each street intersection when construction of new roadways allows passage by vehicles. Signs SHALL be of an approved size, weather resistant and be maintained until replaced by permanent signs.

Signage as required by the Fire AHJ for First Responder for both interior and exterior of complex, building, business, and / or tenant space(s) showing access to: Mechanical Areas / Sprinkler Riser Control Rooms(s) / Fire Alarm Control Panel(s) / Roof Access.

Key Boxes:

LOCAL REQUIREMENT:  A Knox Box SHALL be installed in a location determined by the Fire AHJ, approximately 5 feet above finished grade.  Applications for Knox boxes are available online through the Knox Box web site. www.Knoxbox.com. We also recommend a dual key box for buildings that are in our outline jurisdiction with a neighboring department that also uses Knox Box.

Locks:

An approved lock (Knox lock) SHALL be installed on gates or similar barriers when required by the fire code official.

Fire Protection Water Supplies:

Required water supply:

An approved water supply capable of supplying the required fire flow for fire protection SHALL be provided to premises upon which facilities, buildings or portions of buildings are hereafter constructed or moved into or within the jurisdiction.

Type of Water Supply:

A water supply SHALL consist of reservoirs, pressure tanks, elevated tanks, water mains or other fixed systems capable of providing the required fire flow.

Private Fire Service Mains:

Private fire service mains and appurtenances SHALL be installed in accordance with NFPA 24 as listed in rule 1301:7-7-47 of the Administrative Code.

Water tanks:

Water tanks for private fire protection SHALL be installed in accordance with NFPA 22 as listed in rule 1301:7-7-47 of the Administrative Code.

Fire Flow:

Fire flow requirements for buildings or portions of buildings and facilities SHALL be determined by an approved method.

Water Supply Test:

The fire code official SHALL be notified prior to the water supply test. Water supply tests SHALL be witnessed by the fire code official or approved documentation of the test SHALL be provided to the fire code official prior to final approval of the water supply system.

LOCAL REQUIREMENT:  Private fire service mains and appurtenances SHALL be 8 inches minimum in diameter, SHALL be installed, inspected, tested, and approved in accordance with NFPA 24 and includes residential subdivisions.  The Fire AHJ SHALL inspect all public and private fire service mains prior to final filling of the pipe trench.  Hydrostatic testing and flushing of all public and private fire service mains SHALL be in accordance with NFPA 24, and SHALL be witnessed by the Fire AHJ and any other responsible AHJ’s (Water Departments, Building Officials, etc.).  Looped Fire Protection Mains are preferable when at all possible.  Plan submittals for review are required by the Fire Marshal prior to waterline approval or installation.

Fire Hydrants:

Where a portion of the facility or building hereafter constructed or moved into or within the jurisdiction is more than 400 feet (122 m) from a hydrant on a fire apparatus access road, as measured by an approved route around the exterior of the facility or building, on-site fire hydrants and mains SHALL be provided where required by the fire code official.

Exceptions:

1. For Group R-3 and Group U occupancies, the distance requirement SHALL be 600 feet (183 m).

2. For buildings equipped throughout with an approved automatic sprinkler system installed in accordance with 1301:7-7-09 of the Administrative Code, the distance requirement SHALL be 600 feet (183 m).

Inspection, Testing and Maintenance:

Fire hydrant systems SHALL be subject to periodic tests as required by the fire code official. Fire hydrant systems SHALL be maintained in an operative condition at all times and SHALL be repaired where defective. Additions, repairs, alterations and servicing SHALL comply with approved standards.

All hydrants SHALL be installed and approved in accordance with NFPA 24 and meet the local water purveyor’s hydrant specifications.

LOCAL REQUIREMENT:  Fire Hydrant Spacing SHALL not exceed 350 feet.  The minimum distance to the building that a fire hydrant can be located is 40 feet.  Fire Hydrants SHALL be located a minimum of 2 feet behind the curb to protect the hydrant from vehicle traffic.

Private Fire Service Mains and Water Tanks:

Private fire service mains and water tanks SHALL be periodically inspected, tested and maintained in accordance with NFPA 25 as listed in rule 1301:7-7-47 of the Administrative Code at the following intervals:

(i) Private fire hydrants (all types): Inspection annually and after each operation; flow test and maintenance annually.

(ii) Fire service main piping: Inspection of exposed, annually; flow test every 5 years.

(iii) Fire service main piping strainers: Inspection and maintenance after each use.

Obstruction:

Unobstructed access to fire hydrants SHALL be maintained at all times. The fire department SHALL not be deterred or hindered from gaining immediate access to fire protection equipment or fire hydrants.

Clear space around hydrants

A 3-foot

Clear space SHALL be maintained around the circumference of fire hydrants except as otherwise required or approved.

Physical Protection:

Where fire hydrants are subject to impact by a motor vehicle, guard posts or other approved means SHALL comply with paragraph (L)(312) of rule 1301:7-7-03 of the Administrative Code.

LOCAL REQUIREMENT:  Fire Hydrants SHALL have a 5-inch “Storz” fitting with blind cap/lanyard attached to the steamer nozzle, plus two additional 2 ½ inch side discharge nozzles equipped with National Standard Hose Thread.  Hydrant operating nuts SHALL be a tapered square.  The Fire AHJ SHALL determine fire hydrant color.  All threads provided for fire department connections to sprinkler systems, standpipe systems, yard hydrants or any other fire hose connection SHALL be compatible with the connections utilized by the local fire department.

Bollard protection SHALL be required (As determined by the Fire AHJ).  Steel bollards filled with concrete SHALL be installed, at a minimum of 3 feet from the hydrant and in a manner so as not to obstruct the clear space in front of the hydrant outlets.  Fences, trees, shrubs, walls, or any other objects SHALL not obstruct hydrants.

Private fire service mains, where paved areas exist, SHALL require a minimum clear area of 10 feet to either side of the fire hydrant, and the area in front of the fire hydrant SHALL be properly signed and striped in the same manner required for Fire Lanes.

FIRE DEPARTMENT CONNECTION:

Fire Department Connection Fittings: Provide a 5-inch “Storz” fitting with a 30-degree down angle for the Fire Department Connection. The supply piping from the Fire Department Connection to the sprinkler/standpipe system SHALL be 5” minimum in diameter.  The top of the fitting SHALL be a minimum of 24 inches and a maximum 36 inches above the finished grade.

Fire Department Connections:  SHALL be located within 50 feet of a fire hydrant located remotely away from the building.  Locations for FDC’s SHALL be determined by the Fire AHJ.  Plan submittal and review is required prior to approval and installation of the FDC.

Signage Indicating the Building Address is required to be located on the Fire Department Connection.  In paved areas, ten (10) feet to either side of the FDC and the area in front of the FDC SHALL be properly signed with the curb painted and pavement striped in the same manner as required for Fire Lanes.  Signage required identifying fire protection equipment and equipment locations SHALL be constructed of durable materials, permanently installed and readily visible. Letters and numbers SHALL contrast with the sign background and have an appropriate width-to-height ratio to permit the sign to be read easily.

Locking Fire Department Connection Caps:  The Fire AHJ requires locking “FDC” caps on Fire Department Connections for water-based fire protection systems.  The responding fire department carries appropriate key wrenches for removal; Applications for Locking Fire Department Connection Caps are available online through Knox box at www.Knox box.com.

FDC testing: All fire department connections are required to pass a hydrostatic test (200# for 2 hours) as required for the building fire suppression system. All FDC lines SHALL be flushed prior to final approval and witness by the fire AHJ.

VEHICLE IMPACT PROTECTION:

Bollard protection SHALL be required (As determined by the Fire AHJ).  Steel bollards filled with concrete SHALL be installed, at a minimum of 3 feet from the hydrant and in a manner so as not to obstruct the clear space in front of the hydrant outlets.

Obstructions such as fences, trees, shrubs, walls, or any other objects SHALL not obstruct the Fire Department Connection (FDC).

Paved areas 10 feet to either side of the FDC, and the area in front of the FDC SHALL be properly signed and striped in the same manner required for Fire Lanes.

FIRE STANDPIPE SYSTEMS:

Standpipe Systems SHALL be installed and comply with all the requirements of NFPA 14 for a Class I Standpipe System, with NST threads equipped with a 2 ½” to 1 ½” reducer and a cap attached with a chain.

An adequate number of Class I standpipes SHALL be installed to allow any point in the building to be reached by a 100-foot length of hose and a 25-foot water stream.  Standpipe connections SHALL be required at all designated Exit locations.

Fire Hose/Fire Hose Racking installations SHALL not be installed for use by building occupants.   Where the building is protected throughout by an approved automatic sprinkler system, hose stations for use by the building occupants SHALL not be required, subject to the approval of the authority having jurisdiction (Fire AHJ),

Shut-Off Valves SHALL be provided at each hose connection location with prior approval of the Fire AHJ.

FIRE SPRINKLER SYSTEMS:

All Fire Sprinkler Systems SHALL be installed in accordance with NFPA 13.

Post-Indicator Valves (PIV) Wrenches SHALL be secured with frangible locks.  Exterior Wall Post-Indicator Valves (WPIV) SHALL also be chained and locked in the OPEN Position with frangible locks.

Inspectors Test Locations for all Fire Sprinkler Systems SHALL be installed in accordance with NFPA 13.

ESFR SPRINKLERED FACILITIES:

The Madison Township Fire Department recommends that the following requirements be implemented within facilities equipped throughout with ESFR Fire Suppression Systems and proposed travel distances in excess of 250 feet.

The recommendations are as follows

Secondary Power Sources be provided for the Fire Pump System, Emergency Egress Lighting, Engineered Mechanical Smoke Exhaust Systems, and Fire Alarm Notification Systems or as otherwise required and approved by the Madison Township Fire Marshal.

NFPA 72 Compliant Automatic Fire Alarm System (Horns, Strobes, Detectors, and Manual Pull Stations) be provided throughout the facility or as otherwise required and approved by the Madison Township Fire Marshal.

Engineered Mechanical Smoke Exhaust systems where approved by the Madison Township Fire Marshal would be an acceptable alternative to smoke and heat vents.  These systems would be manual operation only and independently controlled by the Firefighter’s Smoke Control Panel, to be located in the Fire Pump Control Room.

Engineered Mechanical Smoke Exhaust systems should be designed to allow for a total interior air exchange every 30 minutes.  The required number of Smoke Exhaust Fans will be based on the total cubic feet within the specific fire area.  The minimum allowable fan size SHALL be 15,000 cfm. The preferred fan size would be 45,000 cfm.  (See tables on following pages)

| SMOKE AND HEAT VENTING - 30 MINUTE BUILIDNG AIR EXCHANGE |
| --- |
| SQUARE | ROOF DECK | GROSS | PRODUCT VOLUME | NET CUBIC | SINGLE | TOTAL FANS | TOTAL |
| FOOTAGE | HEIGHT | CUBIC FEET | 25 % DEDUCTION | FEET | FAN CFM | REQUIRED | CFM |
| 300,000 | 32 | 9,600,000 | 2,400,000 | 7,200,000 | 15,000 | 16 | 240,000 |
|  | 35 | 10,500,000 | 2,625,000 | 7,875,000 | 30,000 | 9 | 270,000 |
|  | 40 | 12,000,000 | 3,000,000 | 9,000,000 | 45,000 | 7 | 315,000 |
| 350,000 | 32 | 11,200,000 | 2,800,000 | 8,400,000 | 15,000 | 19 | 270,000 |
|  | 35 | 12,250,000 | 3,062,500 | 9,187,500 | 30,000 | 12 | 360,000 |
|  | 40 | 14,000,000 | 3,500,000 | 10,500,000 | 45,000 | 8 | 360,000 |
| 400,000 | 32 | 12,800,000 | 3,200,000 | 9,600,000 | 15,000 | 22 | 330,000 |
|  | 35 | 14,000,000 | 3,500,000 | 10,500,000 | 30,000 | 12 | 360,000 |
|  | 40 | 16,000,000 | 4,000,000 | 12,000,000 | 45,000 | 9 | 405,000 |
| 450,000 | 32 | 14,400,000 | 3,600,000 | 10,800,000 | 15,000 | 24 | 360,000 |
|  | 35 | 15,750,000 | 3,937,500 | 11,812,500 | 30,000 | 14 | 420,000 |
|  | 40 | 18,000,000 | 4,500,000 | 13,500,000 | 45,000 | 10 | 450,000 |
| 500,000 | 32 | 16,000,000 | 4,000,000 | 12,000,000 | 15,000 | 27 | 405,000 |
|  | 35 | 17,500,000 | 4,375,000 | 13,125,000 | 30,000 | 15 | 450,000 |
|  | 40 | 20,000,000 | 5,000,000 | 15,000,000 | 45,000 | 12 | 540,000 |
| 550,000 | 32 | 17,600,000 | 4,400,000 | 13,200,000 | 15,000 | 30 | 450,000 |
|  | 35 | 19,250,000 | 4,812,500 | 14,437,500 | 30,000 | 17 | 510,000 |
|  | 40 | 22,000,000 | 5,500,000 | 16,500,000 | 45,000 | 13 | 585,000 |
| 600,000 | 32 | 19,200,000 | 4,800,000 | 14,400,000 | 15,000 | 32 | 480,000 |
|  | 35 | 21,000,000 | 5,250,000 | 15,750,000 | 30,000 | 18 | 540,000 |
|  | 40 | 24,000,000 | 6,000,000 | 18,000,000 | 45,000 | 14 | 630,000 |
| 650,000 | 32 | 20,800,000 | 5,200,000 | 15,600,000 | 15,000 | 35 | 525,000 |
|  | 35 | 22,750,000 | 5,687,500 | 17,062,500 | 30,000 | 19 | 570,000 |
|  | 40 | 26,000,000 | 6,500,000 | 19,500,000 | 45,000 | 15 | 675,000 |
| 700,000 | 32 | 22,400,000 | 5,600,000 | 16,800,000 | 15,000 | 38 | 570,000 |
|  | 35 | 24,500,000 | 6,125,000 | 18,375,000 | 30,000 | 21 | 630,000 |
|  | 40 | 28,000,000 | 7,000,000 | 21,000,000 | 45,000 | 16 | 720,000 |
| 750,000 | 32 | 24,000,000 | 6,000,000 | 18,000,000 | 15,000 | 40 | 600,000 |
|  | 35 | 26,250,000 | 6,562,500 | 19,687,500 | 30,000 | 22 | 660,000 |
|  | 40 | 30,000,000 | 7,500,000 | 22,500,000 | 45,000 | 17 | 765,000 |
| 800,000 | 32 | 25,600,000 | 6,400,000 | 19,200,000 | 15,000 | 43 | 645,000 |
|  | 35 | 28,000,000 | 7,000,000 | 21,000,000 | 30,000 | 24 | 720,000 |
|  | 40 | 32,000,000 | 8,000,000 | 24,000,000 | 45,000 | 18 | 810,000 |
| 850,000 | 32 | 27,200,000 | 6,800,000 | 20,400,000 | 15,000 | 46 | 690,000 |
|  | 35 | 29,750,000 | 7,437,500 | 22,312,500 | 30,000 | 25 | 750,000 |
|  | 40 | 34,000,000 | 8,500,000 | 25,500,000 | 45,000 | 19 | 855,000 |

| SMOKE AND HEAT VENTING - 30 MINUTE BUILIDNG AIR EXCHANGE |
| --- |
| SQUARE | ROOF DECK | TOTAL | PRODUCT VOLUME | NET CUBIC | SINGLE | TOTAL | TOTAL |
| FOOTAGE | HEIGHT | CUBIC FEET | 25 % DEDUCTION | FEET | FAN CFM | REQUIRED | CFM |
| 900,000 | 32 | 28,800,000 | 7,200,000 | 21,600,000 | 15,000 | 48 | 720,000 |
|  | 35 | 31,500,000 | 7,875,000 | 23,625,000 | 30,000 | 27 | 810,000 |
|  | 40 | 36,000,000 | 9,000,000 | 27,000,000 | 45,000 | 20 | 900,000 |
| 950,000 | 32 | 30,400,000 | 7,600,000 | 22,800,000 | 15,000 | 51 | 765,000 |
|  | 35 | 33,250,000 | 8,312,500 | 24,937,500 | 30,000 | 28 | 840,000 |
|  | 40 | 38,000,000 | 9,500,000 | 28,500,000 | 45,000 | 22 | 990,000 |
| 1,000,000 | 32 | 32,000,000 | 8,000,000 | 24,000,000 | 15,000 | 54 | 810,000 |
|  | 35 | 35,000,000 | 8,750,000 | 26,250,000 | 30,000 | 30 | 900,000 |
|  | 40 | 40,000,000 | 10,000,000 | 30,000,000 | 45,000 | 23 | 1,035,000 |
| 1,100,000 | 32 | 35,200,000 | 8,800,000 | 26,400,000 | 15,000 | 59 | 885,000 |
|  | 35 | 38,500,000 | 9,625,000 | 28,875,000 | 30,000 | 33 | 990,000 |
|  | 40 | 44,500,000 | 11,125,000 | 33,375,000 | 45,000 | 25 | 1,125,000 |
| 1,200,000 | 32 | 38,400,000 | 9,600,000 | 28,800,000 | 15,000 | 64 | 960,000 |
|  | 35 | 42,000,000 | 10,500,000 | 31,500,000 | 30,000 | 35 | 1,050,000 |
|  | 40 | 48,000,000 | 12,000,000 | 36,000,000 | 45,000 | 27 | 1,215,000 |
| 1,300,000 | 32 | 41,600,000 | 10,400,000 | 31,200,000 | 15,000 | 70 | 1,050,000 |
|  | 35 | 45,500,000 | 11,375,000 | 34,125,000 | 30,000 | 38 | 1,140,000 |
|  | 40 | 52,000,000 | 13,000,000 | 39,000,000 | 45,000 | 29 | 1,305,000 |
| 1,400,000 | 32 | 44,800,000 | 11,200,000 | 33,600,000 | 15,000 | 75 | 1,125,000 |
|  | 35 | 49,000,000 | 12,250,000 | 36,750,000 | 30,000 | 41 | 1,230,000 |
|  | 40 | 56,000,000 | 14,000,000 | 42,000,000 | 45,000 | 32 | 1,440,000 |
| 1,500,000 | 32 | 48,000,000 | 12,000,000 | 36,000,000 | 15,000 | 80 | 1,200,000 |
|  | 35 | 52,500,000 | 13,125,000 | 39,375,000 | 30,000 | 44 | 1,320,000 |
|  | 40 | 60,000,000 | 15,000,000 | 45,000,000 | 45,000 | 34 | 1,530,000 |

FIRE EXTINGUISHERS:

Fire Extinguishers SHALL be provided throughout the facility in accordance with the requirements listed in NFPA 10 and prior approval of the Madison Township Fire Marshal.

ROOF HYDRANTS:

Roof Hydrants Locations SHALL be determined when required request of the Fire AHJ. The

number of roof hydrants required SHALL be based upon 1 roof hydrant for every 250,000 sq. feet

and SHALL be located within 20 feet of the roof access scuttle, hatch, or doorway.

Roof hydrants SHALL be equipped with a double 2 ½” NST valve hose connection.  Water supply piping to the Roof hydrants SHALL be a minimum of 3” in diameter.  The Roof Hydrant SHALL also be equipped with an exterior Post–Indicator Valve (PIV) or Wall Post-Indicator Valve (WPIV) to allow for Fire Department Operation.   This valve SHALL be located in the immediate area of the Roof Hydrant.  A drain valve SHALL also be installed past the PIV or WPIV to allow draining of the unheated portion of the standpipe once the roof hydrant valve has been closed.

Roof Hydrant flow requirements SHALL be included in the calculations for the Fire Sprinkler System/Standpipe System.

Signage required to identify fire protection equipment and equipment locations SHALL be constructed of durable materials, permanently installed and readily visible. Letters and numbers SHALL contrast with the sign background and have an appropriate width-to-height ratio to permit the sign to be read easily.

ROOF ACCESS LADDERS / ROOF HATCH MARKINGS:

Roof Access Ladders SHALL require prior approval of the Fire AHJ.  Emergency Lighting SHALL be provided for illumination of the Roof Access Ladder.  Reflective Materials for Roof Hatches exteriors SHALL be marked with reflective striping so as to make them highly visible under poor light or smoke conditions.  The interior side of the hatch SHALL also be labeled.   Roof hatches SHALL be a minimum of 36” x 42” in size to facilitate Firefighters in full protective gear.

FIRE ALARM SYSTEMS:

- Fire Alarm Systems SHALL require prior review with the Fire AHJ

(Systems SHALL be addressable; which indicates on the panel readout exactly what

device that is in alarm or trouble)

- Fire Alarm System installations and testing SHALL comply with all the requirements in accordance of NFPA 72

- A remote fire alarm enunciator panel located near a front (and/or rear) entry point, by the Knox box and operable by any first responder

- There will be posted at all fire alarm control panel(s) (FACP) (and a copy given to Fire AHJ) a diagram of the facility floor plan(s) with the specific location of all devices as shown on the FACP

- The following information SHALL be posted on FACP & available for FD:

  - central station monitoring company name

  - central station monitoring contact number

  - any & all  necessary account passwords / pass codes related to the occupancy

  - any & all necessary passwords related to the fire alarm systems

  - any & all necessary Fire Alarm Control Panel (FACP) Passwords / Pass Codes

- Horn / Strobe light located outside on exterior of building in place of water gong / bell.

- All fire protection system control valves SHALL be supervised with electronic tamper devices connected to the fire protection supervisory system and to a central station alarm monitoring service.

- All fans Shall be controlled to automatically shut down upon duct or area smoke detector activation or sprinkler system water flow.

CYLINDER / TANK STORAGE of Compressed Gases (Including Propane, Carbon Dioxide, etc.)

As per Rule 38, 30 Ohio Fire Code 2011and SHALL also comply with all requirements under NFPA 58/59.

Emergency Responder Radio Coverage:

All Buildings SHALL have approved radio coverage for emergency responders to meet Rule 5, Section 510 of the 2011 Ohio Fire / Building Code.  Updated on November 2, 2015

Preconstruction Document Packet:

  - Fire Department New Construction Requirements

- Fire Department Contact Information

Fire Marshal Scott Hite (614) 837-7883

- Building Contact Information:

***All Inspection Requests MUST be phoned into the appropriate Building Dept.

Groveport= (614) 830-2045

Canal Winchester = (614) 837-7501

Obetz= (614) 491-1080

- Project Information:

Name:__________________________________________________________________

Assigned Address: ________________________________________________________

Site Contact: Name - _______________________ # = ____________________________

________________________________________________________________________

Projected Life Safety & Final Inspection Dates: _________________________________

This document shall remain on site at all time with the building card for review by

Fire Safety Inspectors.

7/23/2019